## README
Data center delivered-cost model, version 2.1
Companion workbook to: George, C. B. (2026), Data Center Design, Resilience, Reliability and Sustainability: Power, Cooling, Redundancy and Cost for 100–300 MW Campuses, with a Virginia Reference Design Applied Nationwide and Globally. Sanctir working paper, version 1.1, October 24, 2026. License CC BY-NC-ND 4.0.
Purpose: compare three power-supply arrangements for a 200 MW IT campus on a common reliability baseline, with the grid bill built from Dominion Energy Virginia tariff components.
Arrangements: A = grid + diesel backup (N+1); C = grid + dual-fuel gas engines (N+2) + grid-forming battery (recommended configuration); E = onsite engines only (islanded). All three carry the same baseline: 5-minute lithium-ion UPS on IT and CDU load, ride-through-rated cooling drives and transfer settings with an electromagnetic-transient study, and 72 hours of liquid fuel for the installed backup fleet.
Legend: blue text = hardcoded input (edit these on the Inputs and Tariff sheets); black = formula; green = link to another sheet. Yellow fill marks the inputs most likely to change for another site.
Every input is an engineering estimate unless its Source column names a tariff sheet, order or filing. Tariff components are entered as published on each Dominion Energy Virginia tariff sheet and summed by formula into the components the bill uses; the bill calculation applies the GS-5 minimum-billing provisions (85% of contracted transmission and distribution demand, 60% of contracted generation demand).
Outputs on the Model sheet: annual cost by line item, $/MWh, the difference between C and A, and the decomposition of that difference by function. The difference is an indicative modeled cost difference; the common baseline makes the ride-through and UPS service equivalent, but A and C still differ in outage endurance (72 hours of diesel against firm gas plus 72 hours of liquid fuel) and in islanding capability.
Recalculate after changing inputs. The workbook was verified to compute without errors in LibreOffice on October 24, 2026. Model version 2.1 (October 24, 2026) adds the Schedule GS-4 off-peak generation demand charge and Section IX billing-period proration, prices battery charging losses as energy above the energy delivered, and reserves firm gas for arrangement E at the campus peak; these were round-eight review findings (Appendix B).

## Inputs
Input | Value | Unit | Source / note
Campus
Critical IT load | 200 | MW | Reference design, Appendix A
Annual PUE | 1.15 | ratio | Section 6 estimate (1.12–1.20 range)
Peak facility load (billing demand) | 240 | MW | Appendix A
Capital recovery factor | 10% | per year | About 20 years at 8%
Hours per year | 8760 | h
Common baseline (identical in A, C and E)
UPS-protected load (IT plus CDU pumps) | 210 | MW | Section 9
UPS installed cost | 450 | $/kW | Engineering estimate, lithium-ion double-conversion UPS with switchgear
UPS fixed O&M | 5 | $/kW-yr | Engineering estimate
Ride-through package (drives, controls, EMT study) | 15000000 | $ one-off | Engineering estimate; Section 8 steps 1–4
Liquid fuel storage, 72 hours | 40000 | $/MW of backup | Engineering estimate; tanks, containment, fuel polishing
Configuration A: diesel backup
Diesel fleet (N+1) | 264 | MW | Appendix A basis: 240 MW peak plus one spare 24 MW block
Diesel installed cost | 800 | $/kW | Engineering estimate, Tier 4-equivalent gensets with paralleling switchgear
Diesel fixed O&M | 8 | $/kW-yr | Engineering estimate
Test and emergency run hours | 60 | h/yr | NFPA 110 monthly exercise plus emergencies
Diesel generation cost | 200 | $/MWh | About 70 gal/MWh at $2.90/gal
Configuration C: dual-fuel engines and battery
Gas engine fleet (16 × 20 MW, N+2) | 320 | MW | Appendix A
Engine installed cost incl. SCR | 2000 | $/kW | Engineering estimate; Section 4 range $1,500–2,500
Engine fixed O&M | 15 | $/kW-yr | Engineering estimate
Engine heat rate | 8.5 | MMBtu/MWh | HHV; about 40% efficiency
Outage and emergency run hours | 100 | h/yr | Henrico code limits operation to outages and testing
Engine variable O&M | 15 | $/MWh | Engineering estimate
Gas lateral and metering | 25000000 | $ one-off | Engineering estimate; Section 5
Firm gas transportation reservation | 0.4 | $/Dth-day | Engineering estimate for a Transco Zone 5 lateral; confirm against the pipeline tariff
Battery power | 120 | MW | Appendix A
Battery energy | 240 | MWh | Appendix A
Battery installed cost | 400 | $/kWh | Engineering estimate, grid-forming inverters included
Battery fixed O&M | 10 | $/kW-yr | Engineering estimate
Battery augmentation | 1.5% | fraction of capex per year | Engineering estimate
Battery full cycles per year (energy delivered) | 250 | cycles | Curtailment, peak shaving and testing; charging losses are the energy drawn above the energy delivered, (1/RTE - 1) per cycle
Battery round-trip efficiency | 0.88 | ratio | Engineering estimate
Capacity-credit scenario: generation demand reduction | 100 | MW | Scenario only; no current Dominion tariff provision grants it (Section 12)
Configuration E: onsite engines only
Engine fleet (islanded) | 360 | MW | Section 13
Engine heat rate | 8.5 | MMBtu/MWh | As above
Engine variable O&M | 15 | $/MWh | As above
Cases
Gas price, base and uncapped cases | 4.5 | $/MMBtu | Henry Hub plus basis, engineering assumption
Gas price, high-gas case | 8 | $/MMBtu | Stress case
Rider A fuel-factor multiplier, high-gas case | 1.5 | ratio | Assumption: gas-fired generation and gas-indexed purchased power make up roughly half to two-thirds of the fuel factor; see Tariff sheet note
PJM uncapped Dominion-zone price (2027/28 simulation) | 542.83 | $/MW-day | PJM 2027/28 BRA report appendix
PJM 2027/28 clearing price (cap) | 333.44 | $/MW-day | PJM 2027/28 BRA results

## Tariff
Dominion Energy Virginia component | Rate | Unit | Source (tariff sheet, order or filing) and note
Published components (enter as on the tariff sheet)
Component | Rate | Unit | Effective; source and note
Basic customer charge (Schedule GS-4, transmission voltage) | 343.54 | $/month | Effective 01-01-2026. Schedule GS-4, Large General Service, filed 12-09-25, effective for usage on and after 01-01-26 (dominionenergy.com, large-business/schedule-gs4.pdf)
Distribution demand charge (zero at 69 kV and above) | 0 | $/kW-month | Effective 01-01-2026. Schedule GS-4: $2.717/kW for the first 5,000 kW and $2.076/kW thereafter at primary voltage; not charged at delivery voltages of 69 kV and above. The reference design connects at 230 kV.
Transmission demand charge, base | 2.31 | $/kW-month | Effective 01-01-2026. Schedule GS-4, transmission voltage, on on-peak electricity-supply demand
Generation demand charge, on-peak | 9.28 | $/kW-month | Effective 01-01-2026. Schedule GS-4 II.B.1, transmission voltage, on on-peak electricity-supply demand (Section VI). From January 1, 2027, Section VIII applies to customers of 25 MW or more that do not qualify for GS-5: generation demand is the highest of the measured on-peak demand, 75% of the prior summer's peak, or 60% of contracted demand, and when the 60% floor controls the charge excludes PJM capacity expense.
Generation demand charge, off-peak (on off-peak demand above 90% of on-peak demand, Section VII) | 0.558 | $/kW-month | Effective 01-01-2026. Schedule GS-4 II.B.2 and VII. For a flat 240 MW load the billable off-peak demand is 10% of on-peak demand, 24,000 kW.
Rider T1 (transmission) | 4.673 | $/kW-month | Effective 09-01-2026. Rider T1 sheet, effective 09-01-26 (dominionenergy.com, shared/rider-t1.pdf); $4.729/kW at primary voltage. Billed on on-peak electricity-supply demand like the base transmission charge; grouped with transmission demand for the GS-5 85% minimum.
Rider E (environmental) | 0.145 | $/kW-month | Effective 11-01-2025. Rider E sheet (shared/rider-e.pdf). Riders E, GEN, SNA, CERC, SMR, CE and OSW are billed on on-peak electricity-supply demand; grouped with generation demand for the GS-5 60% minimum in the credit scenario.
Rider GEN (generation facilities) | 0.967 | $/kW-month | Effective 04-01-2026. Rider GEN sheet (shared/rider-gen.pdf)
Rider SNA (Surry and North Anna life extension) | 0.886 | $/kW-month | Effective 09-01-2026. Rider SNA sheet (shared/rider-sna.pdf)
Rider CERC (Chesterfield Energy Reliability Center) | 0.158 | $/kW-month | Effective 03-01-2026. Rider CE sheet (shared/rider-ce.pdf). Non-bypassable; the Exhibit of Applicable Riders notes exceptions for qualifying accelerated renewable energy buyers and certain grandfathered competitive-supply customers. The modeled customer is a bundled-service customer with no exemption.
Rider SMR (small modular reactor development) | 0.04 | $/kW-month | Effective 09-01-2026. Rider SMR sheet (shared/rider-smr.pdf), through 08-31-27
Rider CE (clean energy, non-bypassable) | 0.499 | $/kW-month | Effective 05-01-2026. Rider CE sheet (shared/rider-ce.pdf). Non-bypassable; the Exhibit of Applicable Riders notes exceptions for qualifying accelerated renewable energy buyers and certain grandfathered competitive-supply customers. The modeled customer is a bundled-service customer with no exemption.
Rider OSW (Coastal Virginia Offshore Wind, non-bypassable) | 2.396 | $/kW-month | Effective 09-01-2026. Rider OSW sheet (shared/rider-osw.pdf)
Rider DIST (distribution projects; zero at transmission voltage) | 0 | $/kW-month | Effective 06-01-2026. Rider DIST sheet (shared/rider-dist.pdf); $0.311/kW on distribution demand at primary voltage
Generation energy charge, blended on-peak and off-peak | 0.00386 | $/kWh | Effective 01-01-2026. Schedule GS-4: 0.4648 cents/kWh on-peak, 0.3299 cents/kWh off-peak. On-peak hours are weekdays 10 a.m. to 10 p.m. June through September and 7 a.m. to 10 p.m. October through May, about 3,650 of 8,760 hours (41.7%); a flat load pays the hour-weighted blend.
Distribution energy charge | 0.000157 | $/kWh | Effective 01-01-2026. Schedule GS-4, transmission voltage
Rider A (fuel factor), interim | 0.037648 | $/kWh | Effective 07-01-2026. Rider A sheet filed 05-29-26, effective 07-01-26 (shared/rider-a.pdf), Case PUR-2026-00058. PJM capacity cost is recovered in base rates, not through Rider A (SCC final order, Case PUR-2025-00058, November 25, 2025).
Rider CCR (coal combustion residuals, non-bypassable) | 0.001765 | $/kWh | Effective 01-01-2026. Rider CCR sheet (shared/rider-ccr.pdf)
Rider RPS (renewable portfolio standard, non-bypassable) | 0.00552 | $/kWh | Effective 09-01-2026. Rider RPS sheet (shared/rider-rps.pdf). Non-bypassable; same exceptions as Rider CE for accelerated renewable energy buyers. The modeled customer is a bundled-service customer with no exemption.
Rider C1A (peak shaving) | 0.000212 | $/kWh | Effective 09-01-2026. Rider C1A sheet (shared/rider-c1a.pdf)
Rider C4A (energy efficiency) | 0.000698 | $/kWh | Effective 09-01-2026. Rider C4A sheet (shared/rider-c4a.pdf)
Rider RGGI and Rider PIPP | 0 | $/kWh | Effective 04-01-2025. Both at 0.0000 cents/kWh on the current sheets
Deferred fuel cost charge (2023 securitization bonds), all kWh | 0.002901 | $/kWh | Effective 08-01-2026. Deferred Fuel Cost Charge sheet, filed 06-15-26, effective 08-01-26 (shared/deferred-fuel-cost-charge-tariff.pdf): non-bypassable, 0.2901 cents/kWh on all kWh under Schedule GS-4 among others. Read on October 24, 2026.
Components as used in the bill (formulas summing the rows above)
Basic customer charge | 343.54 | $/month
Distribution demand charge (on T&D billing demand) | 0 | $/kW-month
Transmission demand charge, base (on T&D billing demand) | 2.31 | $/kW-month
Generation demand charge, on-peak (on generation billing demand) | 9.28 | $/kW-month
Generation demand charge, off-peak (on off-peak demand above the threshold share of on-peak demand) | 0.558 | $/kW-month
Transmission-demand riders (Rider T1) | 4.673 | $/kW-month
Generation-demand riders (E, GEN, SNA, CERC, SMR, CE, OSW, DIST) | 5.091 | $/kW-month
Base energy charges (generation blended plus distribution) | 0.004017 | $/kWh
Fuel factor (Rider A) | 0.037648 | $/kWh
Energy-based riders (CCR, RPS, C1A, C4A, RGGI, PIPP, deferred fuel) | 0.011096 | $/kWh
Off-peak demand threshold (share of on-peak demand above which off-peak demand is billed) | 90% | fraction | Schedule GS-4 Section VII
Billing days in the year (Schedule GS-4 Section IX prorates the schedule charges by days/30) | 365 | days | Schedule GS-4 Section IX; riders are billed at 12 months (no proration clause on the Rider T1 sheet)
GS-5 minimum billing, transmission and distribution demand | 85% | fraction of contracted demand | SCC final order, PUR-2025-00058, November 25, 2025; Schedule GS-4 Section VIII from January 1, 2027
GS-5 minimum billing, generation demand | 60% | fraction of contracted demand | SCC final order, PUR-2025-00058
Share of the generation demand charge scaled with the PJM capacity price (uncapped case) | 100% | fraction | Assumption; the generation demand charge ($111/kW-yr) is close to the 2027/28 PJM capped price ($122/kW-yr), so 100% is equivalent to passing the full uncapped increment through. See note below.
Bill calculation for the reference campus (annual)
Energy (MWh/yr) | 2014800
Billing demand, T&D (kW, after 85% minimum) | 240000
Billing demand, generation (kW, no credit) | 240000
Billing demand, generation (kW, credit scenario) | 144000
Billable off-peak demand (kW, no credit) | 24000
Billable off-peak demand (kW, credit scenario) | 110400
Schedule charge months per year (billing days / 30) | 12.1667
Customer charge (prorated) | 4179.7367
Distribution demand (prorated) | 0
Transmission demand, base (prorated) | 6745200
Transmission-demand riders | 13458240
Generation demand, on-peak (prorated) | 27097600
Generation demand, off-peak (prorated) | 162936
Generation-demand riders | 14662080
Base energy charges | 8093451.6
Fuel factor (Rider A) | 75853190.4
Energy-based riders | 22356220.8
Annual bill, base case (no credit) | 168433098.5367
Effective rate ($/MWh) | 83.5979
Effective rate (¢/kWh) | 8.3598
Basis: Dominion Energy Virginia Schedule GS-4 (Large General Service) at transmission delivery voltage, with the riders listed in the Exhibit of Applicable Riders filed 09-16-26 and effective 09-01-26. Schedule GS-5, the rate class created by the SCC's final order in Case PUR-2025-00058 (November 25, 2025) for customers of 25 MW or more at a 75% load factor, applies to agreements signed on or after January 1, 2027; its unit rates had not been published at the status date (compliance tariffs are due 45 days before the effective date), so GS-4 transmission-voltage rates are the proxy and the GS-5 minimum-billing provisions (85% of contracted transmission and distribution demand, 60% of contracted generation demand, PJM capacity excluded from the 60% floor) are applied. Tariff sheets were read on dominionenergy.com on October 23, 2026 (Tier 1 for the rates; the mapping of the sheets to a GS-5 bill is the author's).
Not modeled: the Virginia consumption tax and local utility taxes, the reactive (rkVA) demand charge, excess-facilities charges, Rider D (tax gross-up on contributions in aid of construction), GS-5 collateral ($1.5 million per MW, reducible by 70%), and the direct-connect transmission contribution ordered in Case PUR-2026-00056 (July 31, 2026), whose implementing line-extension policy is pending and for which no amounts have been set. Billing-period proration: Schedule GS-4 Section IX multiplies the customer charge and the on-peak, off-peak and transmission demand charges by the days in the billing period divided by 30, so over 365 days those charges total 365/30 months rather than 12; the model applies that factor to the Schedule GS-4 charges and bills the riders at 12 months (the Rider T1 sheet states no proration clause; the other rider sheets were not checked for one). The high-gas case raises the Rider A fuel factor by 50%, an assumption rather than a derivation from Dominion's fuel mix (gas-fired generation and gas-indexed purchased power account for roughly half to two-thirds of the factor; the factor rose from 2.07 to 3.76 cents/kWh between July 2024 and July 2026); base energy and demand rates do not move with gas prices between rate cases. The uncapped-capacity case escalates the whole generation demand charge ($111/kW-yr, close to the 2027/28 PJM capped price of $122/kW-yr) by the ratio of PJM's uncapped Dominion-zone simulation ($542.83/MW-day) to the capped clearing price ($333.44/MW-day); because only part of that charge is purchased-capacity expense, this is an upper-bound stress case, not an estimate of the bill an uncapped auction would produce. The capacity-credit scenario lowers generation billing demand to the 60% floor (144 MW) and prices the floor at the full generation demand charge; Schedule GS-4 VIII.B.2 excludes PJM capacity expense when the floor controls, which cannot be implemented without the unpublished capacity component, so the scenario bill is an upper bound of a floor bill.

## Model
Annual cost ($) by configuration and case; formulas reference Inputs and Tariff
Line item | A ¦ Base | C ¦ Base | C+credit ¦ Base | E ¦ Base | A ¦ High gas ($8/MMBtu) | C ¦ High gas ($8/MMBtu) | C+credit ¦ High gas ($8/MMBtu) | E ¦ High gas ($8/MMBtu) | A ¦ Uncapped capacity | C ¦ Uncapped capacity | C+credit ¦ Uncapped capacity | E ¦ Uncapped capacity
Grid bill (tariff components) | 168433098.5367 | 168433098.5367 | 152315796.1367 | 0 | 206359693.7367 | 206359693.7367 | 190242391.3367 | 0 | 185449552.6633 | 185449552.6633 | 162525668.6127 | 0
UPS (capital recovery + O&M) | 10500000 | 10500000 | 10500000 | 10500000 | 10500000 | 10500000 | 10500000 | 10500000 | 10500000 | 10500000 | 10500000 | 10500000
Ride-through package (capital recovery) | 1500000 | 1500000 | 1500000 | 1500000 | 1500000 | 1500000 | 1500000 | 1500000 | 1500000 | 1500000 | 1500000 | 1500000
Backup fleet capital and fixed O&M | 24288000 | 72580000 | 72580000 | 81340000 | 24288000 | 72580000 | 72580000 | 81340000 | 24288000 | 72580000 | 72580000 | 81340000
Firm gas transportation reservation | 0 | 9530880 | 9530880 | 7148160 | 0 | 9530880 | 9530880 | 7148160 | 0 | 9530880 | 9530880 | 7148160
Fuel and variable O&M | 3168000 | 1704000 | 1704000 | 107288100 | 3168000 | 2656000 | 2656000 | 167228400 | 3168000 | 1704000 | 1704000 | 107288100
Battery capital, O&M, augmentation and losses | 0 | 12671680.9091 | 12671680.9091 | 12675681.8182 | 0 | 12825695.4545 | 12825695.4545 | 12919090.9091 | 0 | 12671680.9091 | 12671680.9091 | 12675681.8182
Total annual cost ($) | 207889098.5367 | 276919659.4458 | 260802357.0458 | 220451941.8182 | 245815693.7367 | 315952269.1912 | 299834966.7912 | 280635650.9091 | 224905552.6633 | 293936113.5724 | 271012229.5218 | 220451941.8182
Delivered cost ($/MWh) | 103.181 | 137.4428 | 129.4433 | 109.4163 | 122.005 | 156.8157 | 148.8162 | 139.2871 | 111.6267 | 145.8885 | 134.5107 | 109.4163
Difference C minus A ($/MWh) |  | 34.2617 | 26.2623 |  |  | 34.8107 | 26.8112 |  |  | 34.2617 | 22.884
Difference C minus A ($ per year) |  | 69030560.9091 | 52913258.5091 |  |  | 70136575.4545 | 54019273.0545 |  |  | 69030560.9091 | 46106676.8584
Decomposition of the base-case difference C minus A ($/MWh)
Engines in place of diesel (capital, O&M, lateral, tanks) | 23.9686
Firm gas transportation | 4.7304
Engine run hours less diesel test hours | -0.72662
Battery (capital, O&M, augmentation, losses) | 6.2893
Total difference, no capacity credit | 34.2617
Capacity-credit scenario (reduction, if a tariff mechanism grants it) | -7.9995
Total difference, credit scenario | 26.2623
Notes: A and C share the UPS, ride-through package and fuel-storage baseline, so the difference reflects the engine fleet, firm gas, the battery and their operating costs. A and C still differ in outage endurance and islanding capability; the difference is an indicative modeled cost, not a measured price of resilience. E has no grid bill and no ride-through obligation but carries the full fuel cost and a major-source permit (Section 13).

## Design conditions
Key | Station | WMO | 0.4% DB (°C) | 1% DB (°C) | 2% DB (°C) | MCWB at 0.4% (°C) | TMYx max (°C) | Hours >27°C | Hours >30°C | Hours >32°C | Hours >34°C | Hours >36°C | Hours >38°C | Hours >40°C
Richmond | Richmond Intl AP | 724010 | 35 | 33.6 | 32.3 | 24.2 | 37.8 | 1127 | 468 | 228 | 66 | 12 | 0 | 0
Dulles | Washington Dulles Intl AP | 724030 | 34 | 32.6 | 31.4 | 23.6 | 37.2 | 896 | 361 | 158 | 35 | 8 | 0 | 0
Atlanta | Atlanta Hartsfield-Jackson Intl AP | 722190 | 34.2 | 33.1 | 32 | 23.1 | 35 | 1320 | 489 | 203 | 7 | 0 | 0 | 0
Houston | Houston Bush Intercontinental AP | 722430 | 36.8 | 35.6 | 34.6 | 24.8 | 37.8 | 2477 | 1226 | 786 | 239 | 51 | 0 | 0
Dallas | Dallas-Fort Worth Intl AP | 722590 | 38.9 | 37.5 | 36.2 | 23.5 | 38.3 | 2367 | 1288 | 892 | 458 | 152 | 3 | 0
Phoenix | Phoenix Sky Harbor Intl AP | 722780 | 44 | 42.8 | 41.7 | 20.8 | 46.1 | 3839 | 2907 | 2399 | 1753 | 1308 | 815 | 409
LasVegas | Las Vegas McCarran Intl AP | 723860 | 42.9 | 41.6 | 40.5 | 19.4 | 43.9 | 3111 | 2276 | 1813 | 1233 | 890 | 501 | 226
Reno | Reno-Tahoe Intl AP | 724880 | 36.4 | 35.1 | 33.6 | 16.1 | 39.4 | 1049 | 614 | 437 | 201 | 70 | 6 | 0
Chicago | Chicago O'Hare Intl AP | 725300 | 32.9 | 31.5 | 30.1 | 23.2 | 37.8 | 610 | 202 | 72 | 17 | 7 | 0 | 0
Columbus | Columbus John Glenn Intl AP | 724280 | 32.8 | 31.6 | 30.3 | 22.9 | 33.3 | 631 | 150 | 37 | 0 | 0 | 0 | 0
DesMoines | Des Moines Intl AP | 725460 | 34 | 32.5 | 31 | 24.4 | 37.2 | 835 | 265 | 102 | 21 | 7 | 0 | 0
Portland | Portland Intl AP | 726980 | 33.5 | 31.2 | 29.2 | 19.7 | 36.1 | 411 | 124 | 51 | 18 | 3 | 0 | 0
MosesLake | Moses Lake Grant County Intl AP (for Quincy) | 727827 | 37 | 35.1 | 33.1 | 19.1 | 41.7 | 895 | 457 | 285 | 148 | 100 | 46 | 10
Boise | Boise Air Terminal | 726810 | 37.3 | 35.8 | 34.2 | 17.4 | 39.4 | 983 | 537 | 363 | 194 | 87 | 12 | 0
SaltLake | Salt Lake City Intl AP | 725720 | 37.1 | 35.8 | 34.4 | 16.8 | 38.3 | 1161 | 684 | 452 | 221 | 115 | 6 | 0
Dublin | Dublin AP | 039690 | 22.2 | 20.7 | 19.6 | 17.1 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
London | London Heathrow | 037720 | 28.9 | 26.6 | 24.8 | 18.7 | 32 | 74 | 16 | 0 | 0 | 0 | 0 | 0
Amsterdam | Amsterdam Schiphol | 062400 | 28.3 | 25.9 | 24 | 20 | 31 | 33 | 3 | 0 | 0 | 0 | 0 | 0
Frankfurt | Frankfurt AP | 106370 | 32.1 | 29.8 | 27.9 | 19.8 | 35 | 241 | 80 | 34 | 2 | 0 | 0 | 0
Paris | Paris-Orly | 071490 | 31.8 | 29.6 | 27.6 | 20.1 | 36.3 | 212 | 67 | 32 | 13 | 2 | 0 | 0
Madrid | Madrid-Barajas | 082210 | 37.3 | 36 | 34.5 | 18.2 | 38.5 | 1158 | 716 | 452 | 270 | 97 | 4 | 0
Stockholm | Stockholm Arlanda | 024600 | 27.3 | 25.4 | 23.7 | 18 | 29.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Oslo | Oslo Gardermoen | 013840 | 26.3 | 24.5 | 22.5 | 16.6 | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 0
Helsinki | Helsinki-Vantaa | 029740 | 27.7 | 25.9 | 24.1 | 18.8 | 30.7 | 40 | 6 | 0 | 0 | 0 | 0 | 0
Singapore | Singapore Changi | 486980 | 33.4 | 32.9 | 32.4 | 26.1 | 34 | 5339 | 1448 | 144 | 0 | 0 | 0 | 0
Johor | Johor (Senai) AP | 486790 | 34.2 | 33.5 | 33.1 | 27.4 | 35 | 3255 | 1554 | 458 | 14 | 0 | 0 | 0
Tokyo | Tokyo (Chiyoda) | 476620 | 33.8 | 32.7 | 31.6 | 25.9 | 35.3 | 1092 | 353 | 139 | 27 | 0 | 0 | 0
Osaka | Osaka | 477720 | 34.6 | 33.6 | 32.6 | 25.1 | 37.4 | 1520 | 562 | 278 | 82 | 17 | 0 | 0
Seoul | Seoul | 471080 | 32.9 | 31.5 | 30.2 | 24.5 | 35.7 | 936 | 277 | 94 | 15 | 0 | 0 | 0
Mumbai | Mumbai Shivaji Intl AP | 430030 | 36.1 | 35.1 | 34.3 | 22.3 | 38.4 | 5516 | 2008 | 727 | 129 | 15 | 2 | 0
Chennai | Chennai Intl AP | 432790 | 39 | 37.8 | 36.7 | 26.3 | 41 | 5907 | 2778 | 1523 | 658 | 203 | 37 | 3
Hyderabad | Hyderabad Rajiv Gandhi Intl AP | 431285 | 39.8 | 38.6 | 37.5 | 21.7 | 41 | 3089 | 1463 | 840 | 446 | 207 | 61 | 1
Sydney | Sydney Kingsford Smith AP | 947670 | 33.6 | 30.9 | 29.1 | 19.7 | 45.5 | 446 | 158 | 80 | 53 | 34 | 21 | 15
Melbourne | Melbourne Tullamarine AP | 948660 | 35.4 | 32.8 | 30.3 | 18.3 | 40 | 359 | 188 | 88 | 36 | 20 | 7 | 0
AbuDhabi | Abu Dhabi Intl AP | 412170 | 45.2 | 43.9 | 42.6 | 23 | 48 | 5189 | 4081 | 3098 | 2196 | 1467 | 875 | 416
Riyadh | Riyadh King Khalid Intl AP | 404370 | 45 | 44.2 | 43.4 | 19.2 | 46 | 4426 | 3420 | 2771 | 2226 | 1692 | 1244 | 782
SaoPaulo | Sao Paulo Guarulhos AP | 830750 | 32.6 | 31.5 | 30.5 | 21.1 | 37 | 768 | 211 | 57 | 5 | 2 | 0 | 0
Santiago | Santiago Pudahuel AP | 855740 | 32.4 | 31.2 | 30.1 | 17 | 38 | 653 | 177 | 52 | 16 | 4 | 0 | 0
Queretaro | Queretaro | 766250 | 32.2 | 31 | 30 | 15.4 | 34.6 | 709 | 178 | 37 | 2 | 0 | 0 | 0
Nairobi | Nairobi Jomo Kenyatta Intl AP | 637400 | 29.5 | 28.7 | 27.9 | 16.1 | 32 | 305 | 12 | 0 | 0 | 0 | 0 | 0
Johannesburg | Johannesburg OR Tambo Intl AP | 683680 | 29.2 | 28.1 | 27 | 14.7 | 32.4 | 208 | 4 | 1 | 0 | 0 | 0 | 0
Source: design-day (.ddy) and hourly (.epw) files of the TMYx 2011–2025 typical meteorological year set, climate.onebuilding.org, retrieved October 22, 2026. The design-day values are the 2025 ASHRAE Handbook—Fundamentals, Chapter 14, annual cooling design conditions distributed with those files. Hours are counts of hourly dry-bulb readings above each threshold in the 8,760-hour typical year; a typical year understates extreme years.